## Sheet1
Analysis | When | Which | How | Comments
Inverters and Strings | Daily | Perform production analysis at both inverter and string levels | Identify areas or equipment with lower energy production compared to neighboring units | Delta Production from Neighbors Average with relation to the target equipment
Inverters and Strings | Daily | Calculate daily availability and efficiency | > Availability: based on inverter uptime, using the lowest possible data aggregation level > Efficiency: calculated directly from measured inverter data | > Availability: time availability (time operating / total time) > Efficiency: Power AC / Power DC
Trackers – Misalignment | Daily | Verify tracker setpoint versus actual position | > Estimate the energy losses associated with tracker misalignment > Create an alarm for abnormal motor energy consumption, indicating potential mechanical or control issues
PR Analysis | Biweekly | Calculate PR for each equipment/plant, and check what could have caused the losses, when there are any
Anomaly and Low Production detection | Biweekly | Apply different analyses methodologies to detect the variations | > Low Production is already implemented as the "Performance Alerts" > Anomalies could use a methodology like TCHALA